## Table 1
Attention: Christoph Moch Capital Regional District Water Department 479 Island Hwy Victoria, BC Canada V9B 1H7 | [14 empty] | Report Date: 2019/02/13 Report #: R2685529 Version: 1 - Final
MAXXAM JOB #: B909536 Received: 2019/02/07, 14:01 Sample Matrix: DRINKING WATER # Samples Received: 6 | [6 empty] | CERTIFICATE OF ANALYSIS
Date Analyses Quantity Extracted | [14 empty] | Date Analyzed Laboratory Method Analytical Method
Hardness Total (calculated as CaCO3) (1) 6 N/A 2019/02/12 BBY WI-00033 Auto Calc Mercury (Total) by CVAF 6 2019/02/12 2019/02/13 BBY7SOP-00015 BCMOE BCLM Oct2013 m Na, K, Ca, Mg, S by CRC ICPMS (total) 6 N/A 2019/02/12 BBY WI-00033 Auto Calc Elements by CRC ICPMS (total) 2 N/A 2019/02/11 BBY7SOP-00003, EPA 6020b R2 m
Elements by CRC ICPMS (total) 4 2019/02/09 2019/02/11 BBY7SOP-00003 BBY7SOP-00002 | [22 empty] | EPA 6020b R2 m
Remarks: Maxxam Analytics' laboratories are accredited to ISO/IEC 17025:2005 for specific parameters on scopes of accreditation. Unless otherwise noted, procedures used by Maxxam are based upon recognized Provincial, Federal or US method compendia such as CCME, MDDELCC, EPA, APHA.
All work recorded herein has been done in accordance with procedures and practices ordinarily exercised by professionals in Maxxam’s profession using accepted testing methodologies, quality assurance and quality control procedures (except where otherwise agreed by the client and Maxxam in writing). All data is in statistical control and has met quality control and method performance criteria unless otherwise noted. All method blanks are reported; unless indicated otherwise, associated sample data are not blank corrected. Where applicable, unless otherwise noted, Measurement Uncertainty has not been accounted for when stating conformity to the referenced standard.
Maxxam Analytics' liability is limited to the actual cost of the requested analyses, unless otherwise agreed in writing. There is no other warranty expressed or implied. Maxxam has been retained to provide analysis of samples provided by the Client using the testing methodology referenced in this report. Interpretation and use of test results are the sole responsibility of the Client and are not within the scope of services provided by Maxxam, unless otherwise agreed in writing. Maxxam is not responsible for the accuracy or any data impacts, that result from the information provided by the customer or their agent.
Solid sample results, except biota, are based on dry weight unless otherwise indicated. Organic analyses are not recovery corrected except for isotope dilution methods. Results relate to samples tested. When sampling is not conducted by Maxxam, results relate to the supplied samples tested. This Certificate shall not be reproduced except in full, without the written approval of the laboratory. Reference Method suffix “m” indicates test methods incorporate validated modifications from specific reference methods to improve performance. * RPDs calculated using raw data. The rounding of final results may result in the apparent difference. (1) "Total Hardness" was calculated from Total Ca and Mg concentrations and may be biased high (Hardness, or Dissolved Hardness, calculated from Dissolved Ca and Mg, should be used for compliance if available).
Attention: Christoph Moch Capital Regional District Water Department 479 Island Hwy Victoria, BC Canada V9B 1H7 | [14 empty] | Report Date: 2019/02/13 Report #: R2685529 Version: 1 - Final
MAXXAM JOB #: B909536 Received: 2019/02/07, 14:01 Encryption Key | [5 empty] | CERTIFICATE OF ANALYSIS Maxxam 13 Feb 2019 14:07:47
Please direct all questions regarding this Certificate of Analysis to your Project Manager. Debbie Nordbruget, Project Manager Email: DNordbruget@maxxam.ca Phone# (250)385-6112 ==================================================================== This report has been generated and distributed using a secure automated process. Maxxam has procedures in place to guard against improper use of the electronic signature and have the required "signatories", as per section 5.10.2 of ISO/IEC 17025:2005(E), signing the reports. For Service Group specific validation please refer to the Validation Signature Page.
Total Cover Pages : 2
ELEMENTS BY ATOMIC SPECTROSCOPY (DRINKING WATER)
Maxxam ID | [8 empty] | VE9170 | VE9172 |  |  |  | VE9173 |  |  | VE9174
Sampling Date | [8 empty] | 2019/02/06 09:30 | 2019/02/05 10:30 |  |  |  | 2019/02/05 09:30 |  |  | 2019/02/05 09:45
COC Number | [8 empty] | 8464666 | 8464666 |  |  |  | 8464666 |  |  | 8464666
|  |  |  | UNITS | MAC | AO |  | OG | WEST LEECH | CHRIS CREEK |  |  |  | LEECH HEAD |  |  | WEEKS OUT |  |  | RDL |  | QC Batch
Total Metals by ICPMS
Total Aluminum (Al) |  |  |  | ug/L | - | - |  | 100 | 57.3 | 40.2 |  |  |  | 109 |  |  | 232 |  |  | 3 |  | 9318547
Total Antimony (Sb) |  |  |  | ug/L | 6 | - |  | - | <0.50 | <0.50 |  |  |  | <0.50 |  |  | <0.50 |  |  | 0.5 |  | 9318547
Total Arsenic (As) |  |  |  | ug/L | 10 | - |  | - | 0.1 | <0.10 |  |  |  | <0.10 |  |  | 0.11 |  |  | 0.1 |  | 9318547
Total Barium (Ba) |  |  |  | ug/L | 1000 | - |  | - | 3.4 | 2 |  |  |  | 2.9 |  |  | 3.5 |  |  | 1 |  | 9318547
Total Beryllium (Be) |  |  |  | ug/L | - | - |  | - | <0.10 | <0.10 |  |  |  | <0.10 |  |  | <0.10 |  |  | 0.1 |  | 9318547
Total Bismuth (Bi) |  |  |  | ug/L | - | - |  | - | <1.0 | <1.0 |  |  |  | <1.0 |  |  | <1.0 |  |  | 1 |  | 9318547
Total Boron (B) |  |  |  | ug/L | 5000 | - |  | - | <50 | <50 |  |  |  | <50 |  |  | <50 |  |  | 50 |  | 9318547
Total Cadmium (Cd) |  |  |  | ug/L | 5 | - |  | - | <0.010 | <0.010 |  |  |  | <0.010 |  |  | <0.010 |  |  | 0.01 |  | 9318547
Total Chromium (Cr) |  |  |  | ug/L | 50 | - |  | - | <1.0 | <1.0 |  |  |  | <1.0 |  |  | <1.0 |  |  | 1 |  | 9318547
Total Cobalt (Co) |  |  |  | ug/L | - | - |  | - | <0.20 | <0.20 |  |  |  | <0.20 |  |  | <0.20 |  |  | 0.2 |  | 9318547
Total Copper (Cu) |  |  |  | ug/L | - | 1000 |  | - | <0.50 | 0.61 |  |  |  | 0.63 |  |  | 0.77 |  |  | 0.5 |  | 9318547
Total Iron (Fe) |  |  |  | ug/L | - | 300 |  | - | 21 | 15 |  |  |  | 75 |  |  | 193 |  |  | 10 |  | 9318547
Total Lead (Pb) |  |  |  | ug/L | 10 | - |  | - | <0.20 | <0.20 |  |  |  | <0.20 |  |  | <0.20 |  |  | 0.2 |  | 9318547
Total Manganese (Mn) |  |  |  | ug/L | - | 50 |  | - | <1.0 | <1.0 |  |  |  | 1.8 |  |  | 6.1 |  |  | 1 |  | 9318547
Total Molybdenum (Mo) |  |  |  | ug/L | - | - |  | - | <1.0 | <1.0 |  |  |  | <1.0 |  |  | <1.0 |  |  | 1 |  | 9318547
Total Nickel (Ni) |  |  |  | ug/L | - | - |  | - | <1.0 | <1.0 |  |  |  | <1.0 |  |  | <1.0 |  |  | 1 |  | 9318547
Total Selenium (Se) |  |  |  | ug/L | 50 | - |  | - | <0.10 | <0.10 |  |  |  | <0.10 |  |  | <0.10 |  |  | 0.1 |  | 9318547
Total Silicon (Si) |  |  |  | ug/L | - | - |  | - | 2280 | 1870 |  |  |  | 1700 |  |  | 1680 |  |  | 100 |  | 9318547
Total Silver (Ag) |  |  |  | ug/L | - | - |  | - | <0.020 | <0.020 |  |  |  | <0.020 |  |  | <0.020 |  |  | 0.02 |  | 9318547
Total Strontium (Sr) |  |  |  | ug/L | - | - |  | - | 13.4 | 7.6 |  |  |  | 10.2 |  |  | 10 |  |  | 1 |  | 9318547
Total Thallium (Tl) |  |  |  | ug/L | - | - |  | - | <0.010 | <0.010 |  |  |  | <0.010 |  |  | <0.010 |  |  | 0.01 |  | 9318547
Total Tin (Sn) |  |  |  | ug/L | - | - |  | - | <5.0 | <5.0 |  |  |  | <5.0 |  |  | <5.0 |  |  | 5 |  | 9318547
Total Titanium (Ti) |  |  |  | ug/L | - | - |  | - | <5.0 | <5.0 |  |  |  | <5.0 |  |  | 6 |  |  | 5 |  | 9318547
Total Uranium (U) |  |  |  | ug/L | 20 | - |  | - | <0.10 | <0.10 |  |  |  | <0.10 |  |  | <0.10 |  |  | 0.1 |  | 9318547
Total Vanadium (V) |  |  |  | ug/L | - | - |  | - | <5.0 | <5.0 |  |  |  | <5.0 |  |  | <5.0 |  |  | 5 |  | 9318547
Total Zinc (Zn) |  |  |  | ug/L | - | 5000 |  | - | <5.0 | <5.0 |  |  |  | <5.0 |  |  | <5.0 |  |  | 5 |  | 9318547
Total Zirconium (Zr) |  |  |  | ug/L | - | - |  | - | <0.10 | <0.10 |  |  |  | <0.10 |  |  | <0.10 |  |  | 0.1 |  | 9318547
No Fill |  | No Exceedance Exceeds 1 criteria policy/level Exceeds both criteria/levels
Grey
Black
RDL = Reportable Detection Limit
Maxxam ID | [8 empty] | VE9169 | [6 empty] | VE9170
Sampling Date | [8 empty] | 2019/02/06 12:30 | [6 empty] | 2019/02/06 09:30
COC Number | [8 empty] | 8464666 | [6 empty] | 8464666
|  |  |  | UNITS | MAC | AO |  | OG | LEECH TUNNEL |  | RDL |  | QC Batch |  |  | WEST LEECH |  |  | RDL |  | QC Batch
Calculated Parameters
Total Hardness (CaCO3) |  |  |  | mg/L | - | - |  | - | 7.91 |  | 0.5 |  | 9316211 |  |  | 6.46 |  |  | 0.5 |  | 9316211
Elements
Total Mercury (Hg) |  |  |  | ug/L | 1 | - |  | - | <0.0020 |  | 0.002 |  | 9320537 |  |  | <0.0020 |  |  | 0.002 |  | 9320537
Total Metals by ICPMS
Total Aluminum (Al) |  |  |  | ug/L | - | - |  | 100 | 58.8 |  | 3 |  | 9318586
Total Antimony (Sb) |  |  |  | ug/L | 6 | - |  | - | <0.50 |  | 0.5 |  | 9318586
Total Arsenic (As) |  |  |  | ug/L | 10 | - |  | - | <0.10 |  | 0.1 |  | 9318586
Total Barium (Ba) |  |  |  | ug/L | 1000 | - |  | - | 2.7 |  | 1 |  | 9318586
Total Beryllium (Be) |  |  |  | ug/L | - | - |  | - | <0.10 |  | 0.1 |  | 9318586
Total Bismuth (Bi) |  |  |  | ug/L | - | - |  | - | <1.0 |  | 1 |  | 9318586
Total Boron (B) |  |  |  | ug/L | 5000 | - |  | - | <50 |  | 50 |  | 9318586
Total Cadmium (Cd) |  |  |  | ug/L | 5 | - |  | - | <0.010 |  | 0.01 |  | 9318586
Total Chromium (Cr) |  |  |  | ug/L | 50 | - |  | - | <1.0 |  | 1 |  | 9318586
Total Cobalt (Co) |  |  |  | ug/L | - | - |  | - | <0.20 |  | 0.2 |  | 9318586
Total Copper (Cu) |  |  |  | ug/L | - | 1000 |  | - | 0.43 |  | 0.2 |  | 9318586
Total Iron (Fe) |  |  |  | ug/L | - | 300 |  | - | 23.6 |  | 5 |  | 9318586
Total Lead (Pb) |  |  |  | ug/L | 10 | - |  | - | <0.20 |  | 0.2 |  | 9318586
Total Manganese (Mn) |  |  |  | ug/L | - | 50 |  | - | <1.0 |  | 1 |  | 9318586
Total Molybdenum (Mo) |  |  |  | ug/L | - | - |  | - | <1.0 |  | 1 |  | 9318586
Total Nickel (Ni) |  |  |  | ug/L | - | - |  | - | <1.0 |  | 1 |  | 9318586
Total Selenium (Se) |  |  |  | ug/L | 50 | - |  | - | <0.10 |  | 0.1 |  | 9318586
Total Silicon (Si) |  |  |  | ug/L | - | - |  | - | 2160 |  | 100 |  | 9318586
Total Silver (Ag) |  |  |  | ug/L | - | - |  | - | <0.020 |  | 0.02 |  | 9318586
Total Strontium (Sr) |  |  |  | ug/L | - | - |  | - | 14.4 |  | 1 |  | 9318586
Total Thallium (Tl) |  |  |  | ug/L | - | - |  | - | <0.010 |  | 0.01 |  | 9318586
Total Tin (Sn) |  |  |  | ug/L | - | - |  | - | <5.0 |  | 5 |  | 9318586
Total Titanium (Ti) |  |  |  | ug/L | - | - |  | - | <5.0 |  | 5 |  | 9318586
Total Uranium (U) |  |  |  | ug/L | 20 | - |  | - | <0.10 |  | 0.1 |  | 9318586
Total Vanadium (V) |  |  |  | ug/L | - | - |  | - | <5.0 |  | 5 |  | 9318586
Total Zinc (Zn) |  |  |  | ug/L | - | 5000 |  | - | <5.0 |  | 5 |  | 9318586
Total Zirconium (Zr) |  |  |  | ug/L | - | - |  | - | <0.10 |  | 0.1 |  | 9318586
Total Calcium (Ca) |  |  |  | mg/L | - | - |  | - | 2.33 |  | 0.05 |  | 9316624 |  |  | 1.85 |  |  | 0.05 |  | 9316624
Total Magnesium (Mg) |  |  |  | mg/L | - | - |  | - | 0.512 |  | 0.05 |  | 9316624 |  |  | 0.446 |  |  | 0.05 |  | 9316624
No Fill |  | No Exceedance Exceeds 1 criteria policy/level Exceeds both criteria/levels
Grey
Black
RDL = Reportable Detection Limit
Maxxam ID | [8 empty] | VE9169 | [6 empty] | VE9170
Sampling Date | [8 empty] | 2019/02/06 12:30 | [6 empty] | 2019/02/06 09:30
COC Number | [8 empty] | 8464666 | [6 empty] | 8464666
|  |  |  | UNITS | MAC | AO |  | OG | LEECH TUNNEL |  | RDL |  | QC Batch |  |  | WEST LEECH |  |  | RDL |  | QC Batch
Total Potassium (K) |  |  |  | mg/L | - | - |  | - | 0.124 |  | 0.05 |  | 9316624 |  |  | 0.212 |  |  | 0.05 |  | 9316624
Total Sodium (Na) |  |  |  | mg/L | - | 200 |  | - | 1.72 |  | 0.05 |  | 9316624 |  |  | 1.99 |  |  | 0.05 |  | 9316624
Total Sulphur (S) |  |  |  | mg/L | - | - |  | - | <3.0 |  | 3 |  | 9316624 |  |  | <3.0 |  |  | 3 |  | 9316624
No Fill |  | No Exceedance Exceeds 1 criteria policy/level Exceeds both criteria/levels
Grey
Black
RDL = Reportable Detection Limit
Maxxam ID | [8 empty] | VE9171 | [5 empty] | VE9172 |  |  | VE9173 |  |  |  | VE9174
Sampling Date | [8 empty] | 2019/02/05 12:00 | [5 empty] | 2019/02/05 10:30 |  |  | 2019/02/05 09:30 |  |  |  | 2019/02/05 09:45
COC Number | [8 empty] | 8464666 | [5 empty] | 8464666 |  |  | 8464666 |  |  |  | 8464666
|  |  |  | UNITS | MAC | AO |  | OG | CRAGG | RDL |  | QC Batch |  |  | CHRIS CREEK |  |  | LEECH HEAD |  |  |  | WEEKS OUT |  | RDL |  | QC Batch
Calculated Parameters
Total Hardness (CaCO3) |  |  |  | mg/L | - | - |  | - | 6.8 | 0.5 |  | 9316211 |  |  | 6.48 |  |  | 5.94 |  |  |  | 5.41 |  | 0.5 |  | 9316211
Elements
Total Mercury (Hg) |  |  |  | ug/L | 1 | - |  | - | <0.0020 | 0.002 |  | 9320537 |  |  | <0.0020 |  |  | <0.0020 |  |  |  | <0.0020 |  | 0.002 |  | 9320537
Total Metals by ICPMS
Total Aluminum (Al) |  |  |  | ug/L | - | - |  | 100 | 54.8 | 3 |  | 9318586
Total Antimony (Sb) |  |  |  | ug/L | 6 | - |  | - | <0.50 | 0.5 |  | 9318586
Total Arsenic (As) |  |  |  | ug/L | 10 | - |  | - | <0.10 | 0.1 |  | 9318586
Total Barium (Ba) |  |  |  | ug/L | 1000 | - |  | - | 1.7 | 1 |  | 9318586
Total Beryllium (Be) |  |  |  | ug/L | - | - |  | - | <0.10 | 0.1 |  | 9318586
Total Bismuth (Bi) |  |  |  | ug/L | - | - |  | - | <1.0 | 1 |  | 9318586
Total Boron (B) |  |  |  | ug/L | 5000 | - |  | - | <50 | 50 |  | 9318586
Total Cadmium (Cd) |  |  |  | ug/L | 5 | - |  | - | <0.010 | 0.01 |  | 9318586
Total Chromium (Cr) |  |  |  | ug/L | 50 | - |  | - | <1.0 | 1 |  | 9318586
Total Cobalt (Co) |  |  |  | ug/L | - | - |  | - | <0.20 | 0.2 |  | 9318586
Total Copper (Cu) |  |  |  | ug/L | - | 1000 |  | - | 0.41 | 0.2 |  | 9318586
Total Iron (Fe) |  |  |  | ug/L | - | 300 |  | - | 13.2 | 5 |  | 9318586
Total Lead (Pb) |  |  |  | ug/L | 10 | - |  | - | <0.20 | 0.2 |  | 9318586
Total Manganese (Mn) |  |  |  | ug/L | - | 50 |  | - | <1.0 | 1 |  | 9318586
Total Molybdenum (Mo) |  |  |  | ug/L | - | - |  | - | <1.0 | 1 |  | 9318586
Total Nickel (Ni) |  |  |  | ug/L | - | - |  | - | <1.0 | 1 |  | 9318586
Total Selenium (Se) |  |  |  | ug/L | 50 | - |  | - | <0.10 | 0.1 |  | 9318586
Total Silicon (Si) |  |  |  | ug/L | - | - |  | - | 1690 | 100 |  | 9318586
Total Silver (Ag) |  |  |  | ug/L | - | - |  | - | <0.020 | 0.02 |  | 9318586
Total Strontium (Sr) |  |  |  | ug/L | - | - |  | - | 8.5 | 1 |  | 9318586
Total Thallium (Tl) |  |  |  | ug/L | - | - |  | - | <0.010 | 0.01 |  | 9318586
Total Tin (Sn) |  |  |  | ug/L | - | - |  | - | <5.0 | 5 |  | 9318586
Total Titanium (Ti) |  |  |  | ug/L | - | - |  | - | <5.0 | 5 |  | 9318586
Total Uranium (U) |  |  |  | ug/L | 20 | - |  | - | <0.10 | 0.1 |  | 9318586
Total Vanadium (V) |  |  |  | ug/L | - | - |  | - | <5.0 | 5 |  | 9318586
Total Zinc (Zn) |  |  |  | ug/L | - | 5000 |  | - | <5.0 | 5 |  | 9318586
Total Zirconium (Zr) |  |  |  | ug/L | - | - |  | - | <0.10 | 0.1 |  | 9318586
Total Calcium (Ca) |  |  |  | mg/L | - | - |  | - | 1.82 | 0.05 |  | 9316624 |  |  | 1.67 |  |  | 1.61 |  |  |  | 1.42 |  | 0.05 |  | 9316624
Total Magnesium (Mg) |  |  |  | mg/L | - | - |  | - | 0.551 | 0.05 |  | 9316624 |  |  | 0.559 |  |  | 0.464 |  |  |  | 0.45 |  | 0.05 |  | 9316624
No Fill |  |  | No Exceedance Exceeds 1 criteria policy/level Exceeds both criteria/levels
Grey
Black
RDL = Reportable Detection Limit
Maxxam ID | [8 empty] | VE9171 | [5 empty] | VE9172 |  |  | VE9173 |  |  |  | VE9174
Sampling Date | [8 empty] | 2019/02/05 12:00 | [5 empty] | 2019/02/05 10:30 |  |  | 2019/02/05 09:30 |  |  |  | 2019/02/05 09:45
COC Number | [8 empty] | 8464666 | [5 empty] | 8464666 |  |  | 8464666 |  |  |  | 8464666
|  |  |  | UNITS | MAC | AO |  | OG | CRAGG | RDL |  | QC Batch |  |  | CHRIS CREEK |  |  | LEECH HEAD |  |  |  | WEEKS OUT |  | RDL |  | QC Batch
Total Potassium (K) |  |  |  | mg/L | - | - |  | - | <0.050 | 0.05 |  | 9316624 |  |  | 0.051 |  |  | 0.066 |  |  |  | 0.079 |  | 0.05 |  | 9316624
Total Sodium (Na) |  |  |  | mg/L | - | 200 |  | - | 1.3 | 0.05 |  | 9316624 |  |  | 1.3 |  |  | 1.38 |  |  |  | 1.44 |  | 0.05 |  | 9316624
Total Sulphur (S) |  |  |  | mg/L | - | - |  | - | <3.0 | 3 |  | 9316624 |  |  | <3.0 |  |  | <3.0 |  |  |  | <3.0 |  | 3 |  | 9316624
No Fill |  |  | No Exceedance Exceeds 1 criteria policy/level Exceeds both criteria/levels
Grey
Black
RDL = Reportable Detection Limit
GENERAL COMMENTS
Each temperature is the average of up to three cooler temperatures taken at receipt MAC,AO,OG: The guidelines that have been included in this report have been taken from the Canadian Drinking Water Quality Summary Table, February 2017. Criteria A = Maximum Acceptable Concentration (MAC) / Criteria B = Aesthetic Objectives (AO) / Criteria C = Operational Guidance Values (OG) It is recommended to consult these guidelines when interpreting your data since there are non-numerical guidelines that are not included on this report. Turbidity Guidelines: 1. Chemically assisted filtration: less than or equal to 0.3 NTU in 95% of the measurements or 95% of the time each month. Shall not exceed 1.0 NTU at any time. 2. Slow sand / diatomaceous earth filtration: less than or equal to 1.0 NTU in 95% of the measurements or 95% of the time each month. Shall not exceed 3.0 NTU at any time. 3. Membrane filtration: less than or equal to 0.1 NTU in 99% of the measurements made or at least 99% of the time each calendar month. Shall not exceed 0.3 NTU at any time. 4. To ensure effectiveness of disinfection and for good operation of the distribution system, it is recommended that water entering the distribution system have turbidity levels of 1.0 NTU or less. Measurement of Uncertainty has not been accounted for when stating conformity to the selected criteria, where applicable. Results relate only to the items tested.
Package 1 |  | 7.7°C
Page 8 of 12 Maxxam Analytics International Corporation o/a Maxxam Analytics Burnaby: 4606 Canada Way V5G 1K5 Telephone(604) 734-7276 Fax(604) 731-2386
[15 empty] | Matrix Spike | [6 empty] | Spiked Blank |  |  |  |  | Method Blank |  | RPD
QC Batch | Parameter | [9 empty] | Date |  |  |  | % Recovery |  |  |  | QC Limits |  |  | % Recovery |  |  | QC Limits |  | Value | UNITS | Value (%) | QC Limits
9318547 | Total Aluminum (Al) | [9 empty] | 2019-02-11 |  |  |  | 100 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <3.0 | ug/L | 16 | 20
9318547 | Total Antimony (Sb) | [9 empty] | 2019-02-11 |  |  |  | 104 |  |  |  | 80 - 120 |  |  | 104 |  |  | 80 - 120 |  | <0.50 | ug/L
9318547 | Total Arsenic (As) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 102 |  |  | 80 - 120 |  | <0.10 | ug/L
9318547 | Total Barium (Ba) | [9 empty] | 2019-02-11 |  |  |  | 100 |  |  |  | 80 - 120 |  |  | 101 |  |  | 80 - 120 |  | <1.0 | ug/L | 0.81 | 20
9318547 | Total Beryllium (Be) | [9 empty] | 2019-02-11 |  |  |  | 96 |  |  |  | 80 - 120 |  |  | 96 |  |  | 80 - 120 |  | <0.10 | ug/L
9318547 | Total Bismuth (Bi) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 103 |  |  | 80 - 120 |  | <1.0 | ug/L
9318547 | Total Boron (B) | [9 empty] | 2019-02-11 |  |  |  | 94 |  |  |  | 80 - 120 |  |  | 93 |  |  | 80 - 120 |  | <50 | ug/L
9318547 | Total Cadmium (Cd) | [9 empty] | 2019-02-11 |  |  |  | 104 |  |  |  | 80 - 120 |  |  | 104 |  |  | 80 - 120 |  | <0.010 | ug/L | NC | 20
9318547 | Total Chromium (Cr) | [9 empty] | 2019-02-11 |  |  |  | 99 |  |  |  | 80 - 120 |  |  | 101 |  |  | 80 - 120 |  | <1.0 | ug/L | NC | 20
9318547 | Total Cobalt (Co) | [9 empty] | 2019-02-11 |  |  |  | 98 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <0.20 | ug/L
9318547 | Total Copper (Cu) | [9 empty] | 2019-02-11 |  |  |  | 98 |  |  |  | 80 - 120 |  |  | 99 |  |  | 80 - 120 |  | <0.50 | ug/L | NC | 20
9318547 | Total Iron (Fe) | [9 empty] | 2019-02-11 |  |  |  | 106 |  |  |  | 80 - 120 |  |  | 106 |  |  | 80 - 120 |  | <10 | ug/L
9318547 | Total Lead (Pb) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 103 |  |  | 80 - 120 |  | <0.20 | ug/L | NC | 20
9318547 | Total Manganese (Mn) | [9 empty] | 2019-02-11 |  |  |  | 99 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <1.0 | ug/L
9318547 | Total Molybdenum (Mo) | [9 empty] | 2019-02-11 |  |  |  | 104 |  |  |  | 80 - 120 |  |  | 104 |  |  | 80 - 120 |  | <1.0 | ug/L
9318547 | Total Nickel (Ni) | [9 empty] | 2019-02-11 |  |  |  | 99 |  |  |  | 80 - 120 |  |  | 102 |  |  | 80 - 120 |  | <1.0 | ug/L
9318547 | Total Selenium (Se) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <0.10 | ug/L
9318547 | Total Silicon (Si) | [9 empty] | 2019-02-11 |  |  |  | 95 |  |  |  | 80 - 120 |  |  | 92 |  |  | 80 - 120 |  | <100 | ug/L
9318547 | Total Silver (Ag) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 103 |  |  | 80 - 120 |  | <0.020 | ug/L
9318547 | Total Strontium (Sr) | [9 empty] | 2019-02-11 |  |  |  | 98 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <1.0 | ug/L
9318547 | Total Thallium (Tl) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 102 |  |  | 80 - 120 |  | <0.010 | ug/L
9318547 | Total Tin (Sn) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 103 |  |  | 80 - 120 |  | <5.0 | ug/L
9318547 | Total Titanium (Ti) | [9 empty] | 2019-02-11 |  |  |  | 98 |  |  |  | 80 - 120 |  |  | 101 |  |  | 80 - 120 |  | <5.0 | ug/L
9318547 | Total Uranium (U) | [9 empty] | 2019-02-11 |  |  |  | 100 |  |  |  | 80 - 120 |  |  | 102 |  |  | 80 - 120 |  | <0.10 | ug/L
9318547 | Total Vanadium (V) | [9 empty] | 2019-02-11 |  |  |  | 99 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <5.0 | ug/L | NC | 20
9318547 | Total Zinc (Zn) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 102 |  |  | 80 - 120 |  | <5.0 | ug/L | NC | 20
9318547 | Total Zirconium (Zr) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 102 |  |  | 80 - 120 |  | <0.10 | ug/L
9318586 | Total Aluminum (Al) | [9 empty] | 2019-02-11 |  |  |  | 98 |  |  |  | 80 - 120 |  |  | 97 |  |  | 80 - 120 |  | <3.0 | ug/L | 0.91 | 20
9318586 | Total Antimony (Sb) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 102 |  |  | 80 - 120 |  | <0.50 | ug/L | NC | 20
9318586 | Total Arsenic (As) | [9 empty] | 2019-02-11 |  |  |  | 99 |  |  |  | 80 - 120 |  |  | 98 |  |  | 80 - 120 |  | <0.10 | ug/L | NC | 20
9318586 | Total Barium (Ba) | [9 empty] | 2019-02-11 |  |  |  | 98 |  |  |  | 80 - 120 |  |  | 99 |  |  | 80 - 120 |  | <1.0 | ug/L | 0.77 | 20
9318586 | Total Beryllium (Be) | [9 empty] | 2019-02-11 |  |  |  | 95 |  |  |  | 80 - 120 |  |  | 94 |  |  | 80 - 120 |  | <0.10 | ug/L
9318586 | Total Bismuth (Bi) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 101 |  |  | 80 - 120 |  | <1.0 | ug/L
[15 empty] | Matrix Spike | [6 empty] | Spiked Blank |  |  |  |  | Method Blank |  | RPD
QC Batch | Parameter | [9 empty] | Date |  |  |  | % Recovery |  |  |  | QC Limits |  |  | % Recovery |  |  | QC Limits |  | Value | UNITS | Value (%) | QC Limits
9318586 | Total Boron (B) | [9 empty] | 2019-02-11 |  |  |  | 92 |  |  |  | 80 - 120 |  |  | 93 |  |  | 80 - 120 |  | <50 | ug/L | NC | 20
9318586 | Total Cadmium (Cd) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 102 |  |  | 80 - 120 |  | <0.010 | ug/L | NC | 20
9318586 | Total Chromium (Cr) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <1.0 | ug/L | NC | 20
9318586 | Total Cobalt (Co) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 99 |  |  | 80 - 120 |  | <0.20 | ug/L | NC | 20
9318586 | Total Copper (Cu) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 99 |  |  | 80 - 120 |  | <0.20 | ug/L | 1.1 | 20
9318586 | Total Iron (Fe) | [9 empty] | 2019-02-11 |  |  |  | 103 |  |  |  | 80 - 120 |  |  | 107 |  |  | 80 - 120 |  | <5.0 | ug/L | 0.093 | 20
9318586 | Total Lead (Pb) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 101 |  |  | 80 - 120 |  | <0.20 | ug/L | NC | 20
9318586 | Total Manganese (Mn) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 98 |  |  | 80 - 120 |  | <1.0 | ug/L | 1.7 | 20
9318586 | Total Molybdenum (Mo) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 101 |  |  | 80 - 120 |  | <1.0 | ug/L | NC | 20
9318586 | Total Nickel (Ni) | [9 empty] | 2019-02-11 |  |  |  | 103 |  |  |  | 80 - 120 |  |  | 101 |  |  | 80 - 120 |  | <1.0 | ug/L | 4.1 | 20
9318586 | Total Selenium (Se) | [9 empty] | 2019-02-11 |  |  |  | 96 |  |  |  | 80 - 120 |  |  | 97 |  |  | 80 - 120 |  | <0.10 | ug/L | NC | 20
9318586 | Total Silicon (Si) | [9 empty] | 2019-02-11 |  |  |  | 86 |  |  |  | 80 - 120 |  |  | 89 |  |  | 80 - 120 |  | <100 | ug/L | 2.4 | 20
9318586 | Total Silver (Ag) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <0.020 | ug/L | NC | 20
9318586 | Total Strontium (Sr) | [9 empty] | 2019-02-11 |  |  |  | 96 |  |  |  | 80 - 120 |  |  | 96 |  |  | 80 - 120 |  | <1.0 | ug/L
9318586 | Total Thallium (Tl) | [9 empty] | 2019-02-11 |  |  |  | 103 |  |  |  | 80 - 120 |  |  | 103 |  |  | 80 - 120 |  | <0.010 | ug/L
9318586 | Total Tin (Sn) | [9 empty] | 2019-02-11 |  |  |  | 100 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <5.0 | ug/L
9318586 | Total Titanium (Ti) | [9 empty] | 2019-02-11 |  |  |  | 103 |  |  |  | 80 - 120 |  |  | 99 |  |  | 80 - 120 |  | <5.0 | ug/L
9318586 | Total Uranium (U) | [9 empty] | 2019-02-11 |  |  |  | 101 |  |  |  | 80 - 120 |  |  | 100 |  |  | 80 - 120 |  | <0.10 | ug/L | NC | 20
9318586 | Total Vanadium (V) | [9 empty] | 2019-02-11 |  |  |  | 102 |  |  |  | 80 - 120 |  |  | 99 |  |  | 80 - 120 |  | <5.0 | ug/L | NC | 20
9318586 | Total Zinc (Zn) | [9 empty] | 2019-02-11 |  |  |  | NC |  |  |  | 80 - 120 |  |  | 103 |  |  | 80 - 120 |  | <5.0 | ug/L | 1.2 | 20
9318586 | Total Zirconium (Zr) | [9 empty] | 2019-02-11 |  |  |  | 99 |  |  |  | 80 - 120 |  |  | 96 |  |  | 80 - 120 |  | <0.10 | ug/L
9320537 | Total Mercury (Hg) | [9 empty] | 2019-02-13 |  |  |  | 97 |  |  |  | 80 - 120 |  |  | 93 |  |  | 80 - 120 |  | <0.0020 | ug/L | NC | 20
Duplicate: Paired analysis of a separate portion of the same sample. Used to evaluate the variance in the measurement. Matrix Spike: A sample to which a known amount of the analyte of interest has been added. Used to evaluate sample matrix interference. Spiked Blank: A blank matrix sample to which a known amount of the analyte, usually from a second source, has been added. Used to evaluate method accuracy. Method Blank: A blank matrix containing all reagents used in the analytical procedure. Used to identify laboratory contamination. NC (Matrix Spike): The recovery in the matrix spike was not calculated. The relative difference between the concentration in the parent sample and the spike amount was too small to permit a reliable recovery calculation (matrix spike concentration was less than the native sample concentration) NC (Duplicate RPD): The duplicate RPD was not calculated. The concentration in the sample and/or duplicate was too low to permit a reliable RPD calculation (absolute difference <= 2x RDL).
Maxxam Job #: B909536 Report Date: 2019/02/13 | [5 empty] | Capital Regional District Client Project #: LEECH-METALS VALIDATION SIGNATURE PAGE
The analytical data and all QC contained in this report were reviewed and validated by the following individual(s).
Rob Reinert, B.Sc., Scientific Specialist
Maxxam has procedures in place to guard against improper use of the electronic signature and have the required "signatories", as per section 5.10.2 of ISO/IEC 17025:2005(E), signing the reports. For Service Group specific validation please refer to the Validation Signature Page.
Page 11 of 12 Maxxam Analytics International Corporation o/a Maxxam Analytics Burnaby: 4606 Canada Way V5G 1K5 Telephone(604) 734-7276 Fax(604) 731-2386
Page 12 of 12